## OTTV, Roof U-value Template
OTTV Calculation Template
OTTV COMPONENT |  | A | B | C | D | E | F | G | H | I | J | K | L
| Wall Location | Wall Area (m2) | Constant | Solar Absorption Factor (α) | Window to Wall Ratio (WWR) | (1-WWR) | Wall Constr U-Value (Uv) | Glass U-Value (Uf) | Orientation Factor (OF) | Glass Shading Coeff (SC1) | Device Shading Coeff (SC2) | Shading Coefficient SC1 x SC2 (ie columns I x J) | Wall OTTV (ie multiply all shaded cells in the same row) | % of OTTV
HEAT CONDUCTION THROUGH WALLS | Wall 1 | B: 15; G: N/A; H: N/A; I: N/A; J: N/A; K: N/A
| Wall 2 | B: 15; G: N/A; H: N/A; I: N/A; J: N/A; K: N/A
| Wall 3 | B: 15; G: N/A; H: N/A; I: N/A; J: N/A; K: N/A
| Wall 4 | B: 15; G: N/A; H: N/A; I: N/A; J: N/A; K: N/A
| Wall 5 | B: 15; G: N/A; H: N/A; I: N/A; J: N/A; K: N/A
| ∑ Wall Area | A: y; B: Equation for Heat Conduction Through Walls =; G: 15 x α x ( 1 - WWR) Uv; K: ∑
HEAT CONDUCTION THROUGH WINDOWS | Wall 1 |  | 6 | N/A |  | N/A | N/A |  | N/A | N/A | N/A | N/A
| Wall 2 |  | 6 | N/A |  | N/A | N/A |  | N/A | N/A | N/A | N/A
| Wall 3 |  | 6 | N/A |  | N/A | N/A |  | N/A | N/A | N/A | N/A
| Wall 4 |  | 6 | N/A |  | N/A | N/A |  | N/A | N/A | N/A | N/A
| Wall 5 |  | 6 | N/A |  | N/A | N/A |  | N/A | N/A | N/A | N/A
|  |  | Equation for Heat Conduction Through Windows = |  |  |  |  | 6 x WWR x Uf |  |  |  | ∑
SOLAR HEAT GAIN THROUGH WINDOWS | Wall 1 | B: 194; C: N/A; E: N/A; F: N/A; G: N/A
| Wall 2 | B: 194; C: N/A; E: N/A; F: N/A; G: N/A
| Wall 3 | B: 194; C: N/A; E: N/A; F: N/A; G: N/A
| Wall 4 | B: 194; C: N/A; E: N/A; F: N/A; G: N/A
| Wall 5 | B: 194; C: N/A; E: N/A; F: N/A; G: N/A
|  |  | Equation for Solar Heat Gain Through Windows = |  |  |  |  | 194 x WWR x OF x SC |  |  |  | ∑
[10 empty] | ∑ WALL OTTV = |  |  | x
[12 empty] | ∑ WALL AREA = | y
[12 empty] | OTTV = | x / y
OTTV Calculation Example
OTTV COMPONENT |  | A | B | C | D | E | F | G | H | I | J | K | L
| Wall Location | Wall Area (m2) | Constant | Solar Absorption Factor (α) | Window to Wall Ratio (WWR) | (1-WWR) | Wall Constr U-Value (Uv) | Glass U-Value (Uf) | Orientation Factor (OF) | Glass Shading Coeff (SC1) | Device Shading Coeff (SC2) | Shading Coefficient SC1 x SC2 (ie columns I x J) | Wall OTTV (ie multiply all shaded cells in the same row) | % of OTTV
HEAT CONDUCTION THROUGH WALLS | North Wall | 1187.75 | 15 | 0.15 | 0.39 | 0.61 | 0.92 | N/A | N/A | N/A | N/A | N/A | 1499.7719
| South Wall | 2888.95 | 15 | 0.15 | 0.24 | 0.76 | 0.92 | N/A | N/A | N/A | N/A | N/A | 4544.8961
| East Wall | 2010.5 | 15 | 0.15 | 0.43 | 0.57 | 0.92 | N/A | N/A | N/A | N/A | N/A | 2372.189
| West Wall | 2560.7 | 15 | 0.15 | 0.35 | 0.65 | 0.92 | N/A | N/A | N/A | N/A | N/A | 3445.4219
| North East Wall | 723.86 | 15 | 0.15 | 0.46 | 0.54 | 0.88 | N/A | N/A | N/A | N/A | N/A | 773.9511
| ∑ Wall Area | A: 9371.76; B: Equation for Heat Conduction Through Walls =; G: 15 x α x ( 1 - WWR) Uv; K: ∑; L: 12636.23 | 3.102%
HEAT CONDUCTION THROUGH WINDOWS | North Wall | 1187.75 | 6 | N/A | 0.39 | N/A | N/A | 5.25 | N/A | N/A | N/A | N/A | 14591.5088
| South Wall | 2888.95 | 6 | N/A | 0.24 | N/A | N/A | 5.25 | N/A | N/A | N/A | N/A | 21840.462
| East Wall | 2010.5 | 6 | N/A | 0.43 | N/A | N/A | 5.25 | N/A | N/A | N/A | N/A | 27232.2225
| West Wall | 2560.7 | 6 | N/A | 0.35 | N/A | N/A | 5.25 | N/A | N/A | N/A | N/A | 28231.7175
| North East Wall | 723.86 | 6 | N/A | 0.46 | N/A | N/A | 4.6 | N/A | N/A | N/A | N/A | 9190.1266
|  | B: Equation for Heat Conduction Through Windows =; G: 6 x WWR x Uf; K: ∑; L: 101086.0373 | 24.81%
SOLAR HEAT GAIN THROUGH WINDOWS | North Wall | 1187.75 | 194 | N/A | 0.39 | N/A | N/A | N/A | 0.9 | 0.55 | 1 | 0.55 | 44483.2567
| South Wall | 2888.95 | 194 | N/A | 0.24 | N/A | N/A | N/A | 0.92 | 0.55 | 1 | 0.55 | 68061.8131
| East Wall | 2010.5 | 194 | N/A | 0.43 | N/A | N/A | N/A | 1.23 | 0.55 | 0.77 | 0.4235 | 87364.0561
| West Wall | 2560.7 | 194 | N/A | 0.35 | N/A | N/A | N/A | 0.94 | 0.55 | 0.79 | 0.4345 | 71014.349
| North East Wall | 723.86 | 194 | N/A | 0.46 | N/A | N/A | N/A | 1.09 | 0.42 | 0.77 | 0.3234 | 22770.924
|  | B: Equation for Solar Heat Gain Through Windows =; G: 194 x WWR x OF x SC; K: ∑; L: 293694.3988 | 72.09%
|  | I: ∑ WALL OTTV =; L: 407416.6661 | 100%
[12 empty] | ∑ WALL AREA = | 9371.76
[12 empty] | OTTV = | 43.4728
Roof U-Value Calculation Example
R.C. Roof with insulation
Metal Deck Roof with insulation